## Sheet1
Attack # | Start Time | End Time | Attack Point | Start State | Attack | Actual Change | Expected Impact or attacker intent | Unexpected Outcome
0 | 2015-12-28 11:22 | 11:28 | LIT-101 | Water level between L and H | Increase by 1 mm every second | No | Tank Underflow; Damage P-101
1 | 2015-12-28 12:01 | 12:04 | AIT-202 | Value of AIT-202 is >7.05 | Set value of AIT-202 as 6 | No | P-203 turns off; Change in water quality | Impact seen on AIT-504 after two hours at around 14:15. It increased above HH but Drainage did not start
2 | 2015-12-28 12:08 | 12:16 | LIT-301 | Water level between L and H | Water level increased above HH | No | Stop of inflow; Tank underflow; Damage P-301
3 | 2015-12-28 13:10 | 13:26 | DPIT-301 | Value of DPIT is <40kpa | Set value of DPIT as >40kpa | No | Backwash process is started again and again; Normal operation stops; Decrease in water level of tank 401. Increase in water level of tank 301
4 | 2015-12-28 14:16 | 14:19 | FIT-401 | Value of FIT-401 above 1 | Set value of FIT-401 as <0.7 | No | UV shutdown; P-501 turns off; | UV did not shutdown; P-501 did not turn off
5 | 2015-12-28 14:19 | 14:28 | FIT-401 | Value of FIT-401 above 1 | Set value of FIT-401 as 0 | No | UV shutdown; P-501 turns off;
6 | 2015-12-29 11:57 | 12:02 | LIT-301 | Water level between L and H | Decrease water level by 1mm each second | No | Tank Overflow
7 | 2015-12-29 18:11 | 18:15 | AIT-504 | Value of AIT-504 <15 uS/cm | Set value of AIT-504 to 16 uS/cm | No | RO shut down sequence starts after 30 minutes. Water should go to drain. | RO did not shutdown; Water did not go to drain
8 | 2015-12-29 18:16 | 18:22 | AIT-504 | Value of AIT-504 <15 uS/cm | Set value of AIT-504 to 255 uS/cm | No | RO shut down sequence starts after 30 minutes. Water should go to drain. | RO did not shutdown; Water did not go to drain
9 | 2015-12-29 18:30 | 18:42 | LIT-101 | MV-101 is open; LIT-101 between L and H | Keep MV-101 on countinuosly; Value of LIT-101 set as 700 mm | Yes | Tank overflow
10 | 2015-12-29 22:55 | 23:03 | AIT-502, P-501 | UV-01 is on; AIT-502 is <150; P-501 is open | Stop UV-401; Value of AIT502 set as 150; Force P-501 to remain on | Yes | Possible damage to RO | P501 could not be kept on; Reduced output at FIT-502
11 | 2015-12-30 01:43 | 1:54 | DPIT-301 | DPIT-301 is <0.4 bar; MV-302 is on; P-602 is closed | Value of DPIT-301 set to >0.4 bar; Keep MV-302 open; Keep P-602 closed | Yes | System freeze
12 | 2015-12-30 10:02 | 10:12 | LIT-401 | Value of LIT-401 <1000; P-402 is on | Set value of LIT-401 as 1000; P402 is kept on | Yes | Tank underflow
13 | 2015-12-30 17:05 | 17:29 | LIT-301 | P-101 is off; P-102 is on; LIT-301 is between L and H | P-101 is turned on continuosly; Set value of LIT-301 as 801 mm | Yes | Tank 101 underflow; Tank 301 overflow
14 | 2015-12-31 01:17 | 1:45 | LIT-401 | P302 is on, LIT401 Is between L and H | Keep P-302 on contineoulsy; Value of LIT401 set as 600 mm till 1:26:01 | Yes | Tank overflow
15 | 2015-12-31 15:48 | 16:07 | LIT-101 | P-101 is off; MV-101 is off; MV-201 is off; LIT-101 is between L and H; LIT-301 is between L and H | Turn P-101 on continuously; Turn MV-101 on continuously; Set value of LIT-101 as 700 mm; P-102 started itself because LIT301 level became low | Yes | Tank 101 underflow; Tank 301 overflow
16 | 2015-12-31 22:06 | 22:12 | LIT-401 | Water level between L and H | Set LIT-401 to less than L | No | Tank overflow
17 | 2016-01-01 10:36 | 10:46 | LIT-301 | Water level between L and H | Set LIT-301 to above HH | No | Tank underflow; Damage P-302
18 | 2016-01-01 14:21 | 14:29 | LIT-101 | Water level between L and H | Set LIT-101 to above H | No | Tank underflow; Damage P-101
19 | 2016-01-01 22:16 | 22:25 | LIT-101 | Water level between L and H | Set LIT-101 to less than LL | No | Tank overflow
20 | 2015-01-02 11:19 | 11:25 | FIT-502 | P-501 is on; FIT-502 in normal range | Close P-501; Set value of FIT-502 to 1.29 at 11:18:36 | No | Reduced output | P-501 did not turn off; FIT-502 decreased to 0.8; Speed of P-501 increased to 28.50 Hz from 10 Hz during attack.
21 | 2015-01-02 11:32 | 11:36 | AIT-402, AIT-502 | In Normal Range | Set value of AIT402 as 260; Set value of AIT502 to 260 | No | Water goes to drain because of overdosing | Water did not go to the drain
22 | 2015-01-02 11:44 | 11:50 | FIT-401, AIT-502 | In Normal Range | Set value of FIT-401 as 0.5; Set value of AIT-502 as 140 mV | No | UV will shut down and water will go to RO | UV did not shutdown
23 | 2015-01-02 11:52 | 11:57 | FIT-401 | In Normal Range | Set value of FIT-401 as 0 | No | UV will shut down and water will go to RO | P-402 did not close, both should be interlinked
24 | 2015-01-02 13:13 | 13:41 | LIT-301 | Water level between L and H | decrease value by 0.5 mm per second | No | Tank overflow | Rate of decrease in water level reduced after 1:33:25 PM
Single Stage Single Point Attacks
Single Stage Multi Point Attacks
Multi Stage Single Point Attacks
Multi Stage Multi Point Attacks
We changed the value to constant in 26. ICS2 stopped showing the value because it was not changing. When we stopped the attack, it interpolated the points in between. It should have shown a steep increase in level. They will not detect attacks where value is constant